## Sheet1
PFCS Calculator | Ver. 6 (6-Apr-2021)
Power Supply
Output Voltage (V) | 57 | PsRatedVout
Output Power (W) | 100 | PsRatedPout
Powered Fiber Cable
Conductor Gauge (AWG) | 12 AWG | PfcAWG
Ambient Temp (C) | 55C (Sunlight Exposed) | PfcTemp
Extender | 1-port 1Gb PoE PFU-P-C-O-060-01 | ExtenderType
Cable Length Units | Meters | Units
Powered Device #1
PoE Device Class | Class 6 | PdClass1
Max Input Power (W) | 51 | PdMaxPwrSpec1
Min Input Voltage (V) | 42.5 | PdMinVinSpec1
Max Input Voltage (V) | 57 | PdMaxVinSpec1
Cable Type | CS Cat6a F/UTP Outdoor Patch Cord (Recommended) | PdCableType1
Cable Ambient Temp | 55C (Sunlight Exposed) | PdCableTemp1
Cable Length (m) | 50 | PdCableLength1
Powered Device #2
Powered Device Class | Not applicable | PdClass2
Max Input Power (W) | Not applicable | PdMaxPwrSpec2
Min Input Voltage (V) | Not applicable | PdMinVinSpec2
Max Input Voltage (V) | Not applicable | PdMaxVinSpec2
Cable Type | Not applicable | PdCableType2
Cable Ambient Temp | Not applicable | PdCableTemp2
Cable Length (m) | Not applicable | PdCableLength2
Result
Powered Fiber Cable max length (m) | 780.9089 | PfcMaxLength
Additional Information
Worst case supply output current (A) | 1.6946 | PsIout
Worst case supply output power (W) | 96.5905 | PsPout
Extender minimum input voltage (V) | 41.3124 | ExtenderMinVin
Extender minimum output voltage (V) | 50 | ExtenderMinVout
Port 1 maximum output current (A) | 1.0825 | ExtenderMaxIout1
Port 1 maximum output power (W) | 54.126 | ExtenderMaxPout1
Port 1 powered device input voltage (V) | 47.1123 | PdMinVin1
Port 2 maximum output current (A) | Not applicable | ExtenderMaxIout2
Port 2 maximum output power (W) | Not applicable | ExtenderMaxPout2
Port 2 powered device input voltage (V) | Not applicable | PdMinVin2
DISCLAIMER: These calculations are provided for guidance purposes only. They are provided “as is” and should not be relied upon without consultation with and supervision of experienced personnel and a local CommScope representative. CommScope makes no representations or warranties of any kind related to these tools, whether express or implied, and specifically disclaims and excludes any representation or warranty of merchantability, quality, content, completeness, suitability, adequacy, accuracy, noninfringement or fitness for a particular purpose and any representation arising by usage of trade, course of dealing or course of performance. CommScope is under no obligation to issue any upgrades, update specifications or notify users of this tool that changes have been made. The user of these tools assumes all risks associated with such use, and CommScope hereby disclaims any and all liability for damages of any kind resulting from such use.